## pre-calc
LAFmax of seagulls at | 3 | m
|  |  |  | LAFmax / dB(A) | [6 empty] | Criteria
Octave bands central frequency / Hz
LAFmax total / dB | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
86.5594 | 41.0994 | 50.3794 | 57.0994 | 58.5594 | 63.7394 | 85.1594 | 78.6394 | 73.2594 | 60.3794 |  | 42
LAFmax of 1 x human at 3 m
LAFmax / dB(A)
Octave bands central frequency / Hz
LAFmax total / dB | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
70.4576 |  | 31.4576 | 42.4576 | 52.4576 | 63.4576 | 68.7576 | 61.8576 | 54.3576 | 43.5576 |  | 42
LAeq 17:00-18:00 hrs
LAeq / dB
Octave bands central frequency / Hz
LAeq total / dB | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  |  | Adjusted by measured position and the most exposed position
57.6 | 28.3 | 37 | 41.8 | 46.4 | 50.5 | 53.6 | 51.4 | 45.6 | 33.3 | * Adjusted values | 35 | 1
56.6 | 27.3 | 36 | 40.8 | 45.4 | 49.5 | 52.6 | 50.4 | 44.6 | 32.3 | * oringinal measurement
LAeq 06:00-07:00 hrs
LAeq / dB
Octave bands central frequency / Hz
LAeq total / dB | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
51 | 19.8 | 31.4 | 35.9 | 41.7 | 45.1 | 46.6 | 43 | 38 | 26.9 | * Adjusted values | 30
50 | 18.8 | 30.4 | 34.9 | 40.7 | 44.1 | 45.6 | 42 | 37 | 25.9 | * oringinal measurement

## Corner room with seagull
[8 empty] | 12500 | 16000 | 20000 | A
Guest room at the corner
Volume, V /m3 | 40.536
Window area, S /m2 | 4.0425
Wall area, S /m2 | 20.6295
Reverberation Time, T /s | 0.5
Number of vents required
Octave centre frequency | dB(A) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz
Maximum sound level of seagulls at 3m, L1in /dB(A) | 86.0719 | 57.0994 | 58.5594 | 63.7394 | 85.1594 | 78.6394
6/12/4/12/8.8 (44.2) |  | 23 | 31 | 39 | 49 | 48
Equation 1, L2 /dB(A) | 37.3862 | 32.0772 | 25.5372 | 22.7172 | 34.1372 | 28.6172
SRI Wall Type A - insul |  | 48 | 51 | 58 | 65 | 70
Equation 2, L2 /dB(A) | 26.1495 | 14.1556 | 12.6156 | 10.7956 | 25.2156 | 13.6956
Combined noise through window and vent/ dB(A) | 37.7011
Octave centre frequency | dB(A) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz
Maximum sound level of one person shout at 3m, L1in /dB(A) | 70.5905 | 42.4576 | 52.4576 | 63.4576 | 68.7576 | 61.8576
6/12/4/12/8.8 (44.2) |  | 23 | 31 | 39 | 49 | 48
Equation 1, L2 /dB(A) | 25.9443 | 17.4354 | 19.4354 | 22.4354 | 17.7354 | 11.8354
SRI Wall Type A - insul |  | 48 | 51 | 58 | 65 | 70
Equation 2, L2 /dB(A) | 13.9326 | -0.48625 | 6.5138 | 10.5138 | 8.8138 | -3.0862
Combined noise through window and vent/ dB(A) | 26.2094
Octave centre frequency | dB(A) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz
Daytime freefield Noise, L1in /dB(A) | 58.3087 | 42.8 | 47.4 | 51.5 | 54.6 | 52.4 | adjust 1 dB to get same value as sum of 6 octave
6/12/4/12/8.8 (44.2) |  | 23 | 31 | 39 | 49 | 48
Equation 1, L2 /dB(A) | 20.1081 | 17.7778 | 14.3778 | 10.4778 | 3.5778 | 2.3778
SRI Wall Type A - insul |  | 48 | 51 | 58 | 65 | 70
Equation 2, L2 /dB(A) | 5.3539 | -0.14382 | 1.4562 | -1.4438 | -5.3438 | -12.5438
Combined noise through window and vent/ dB(A) | 20.2511
Octave centre frequency | dB(A) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz
Night time freefield noise, L1in /dB(A) | 50.6708 | 35.9 | 41.7 | 45.1 | 46.6 | 43
6/12/4/12/8.8 (44.2) |  | 23 | 31 | 39 | 49 | 48
Equation 1, L2 /dB(A) | 13.5664 | 10.8778 | 8.6778 | 4.0778 | -4.4222 | -7.0222
SRI Wall Type A - insul |  | 48 | 51 | 58 | 65 | 70
Equation 2, L2 /dB(A) | -1.0189 | -7.0438 | -4.2438 | -7.8438 | -13.3438 | -21.9438
Combined noise through window and vent/ dB(A) | 13.715

## Corner room with seagull 160419
[8 empty] | 12500 | 16000 | 20000 | A
Guest room at the corner
Volume, V /m3 | 40.536
Window area, S /m2 | 4.0425
Wall area, S /m2 | 20.6295
Reverberation Time, T /s | 0.5
Number of vents required
Octave centre frequency | dB(A) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz
Maximum sound level of seagulls at 3m, L1in /dB(A) | 86.0719 | 57.0994 | 58.5594 | 63.7394 | 85.1594 | 78.6394
8/12/4/12/8.8 (44.2) |  | 19 | 29 | 41 | 46 | 43
Equation 1, L2 /dB(A) | 40.8673 | 36.0772 | 27.5372 | 20.7172 | 37.1372 | 33.6172
SRI Wall Type A - insul |  | 48 | 51 | 58 | 65 | 70
Equation 2, L2 /dB(A) | 26.1495 | 14.1556 | 12.6156 | 10.7956 | 25.2156 | 13.6956
Combined noise through window and vent/ dB(A) | 41.0114
Octave centre frequency | dB(A) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz
Maximum sound level of one person shout at 3m, L1in /dB(A) | 70.5905 | 42.4576 | 52.4576 | 63.4576 | 68.7576 | 61.8576
8/12/4/12/8.8 (44.2) |  | 19 | 29 | 41 | 46 | 43
Equation 1, L2 /dB(A) | 27.4475 | 21.4354 | 21.4354 | 20.4354 | 20.7354 | 16.8354
SRI Wall Type A - insul |  | 48 | 51 | 58 | 65 | 70
Equation 2, L2 /dB(A) | 13.9326 | -0.48625 | 6.5138 | 10.5138 | 8.8138 | -3.0862
Combined noise through window and vent/ dB(A) | 27.6366
Octave centre frequency | dB(A) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz
Daytime freefield Noise, L1in /dB(A) | 58.3087 | 42.8 | 47.4 | 51.5 | 54.6 | 52.4 | adjust 1 dB to get same value as sum of 6 octave
8/12/4/12/8.8 (44.2) |  | 19 | 29 | 41 | 46 | 43
Equation 1, L2 /dB(A) | 23.2443 | 21.7778 | 16.3778 | 8.4778 | 6.5778 | 7.3778
SRI Wall Type A - insul |  | 48 | 51 | 58 | 65 | 70
Equation 2, L2 /dB(A) | 5.3539 | -0.14382 | 1.4562 | -1.4438 | -5.3438 | -12.5438
Combined noise through window and vent/ dB(A) | 23.3143
Octave centre frequency | dB(A) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz
Night time freefield noise, L1in /dB(A) | 50.6708 | 35.9 | 41.7 | 45.1 | 46.6 | 43
8/12/4/12/8.8 (44.2) |  | 19 | 29 | 41 | 46 | 43
Equation 1, L2 /dB(A) | 16.5702 | 14.8778 | 10.6778 | 2.0778 | -1.4222 | -2.0222
SRI Wall Type A - insul |  | 48 | 51 | 58 | 65 | 70
Equation 2, L2 /dB(A) | -1.0189 | -7.0438 | -4.2438 | -7.8438 | -13.3438 | -21.9438
Combined noise through window and vent/ dB(A) | 16.6452

## Corner room without seagull
[8 empty] | 12500 | 16000 | 20000 | A
Guest room at the corner
Volume, V /m3 | 40.536
Window area, S /m2 | 4.0425
Wall area, S /m2 | 20.6295
Reverberation Time, T /s | 0.5
Number of vents required
Octave centre frequency | dB(A) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz
Maximum sound level of one person shout at 3m, L1in /dB(A) | 70.5905 | 42.4576 | 52.4576 | 63.4576 | 68.7576 | 61.8576
4/12/4/12/4 |  | 20 | 18 | 27 | 43 | 49
Equation 1, L2 /dB(A) | 36.8911 | 20.4354 | 32.4354 | 34.4354 | 23.7354 | 10.8354
SRI Wall Type A - insul |  | 48 | 51 | 58 | 65 | 70
Equation 2, L2 /dB(A) | 13.9326 | -0.48625 | 6.5138 | 10.5138 | 8.8138 | -3.0862
Combined noise through window and vent/ dB(A) | 36.913
Octave centre frequency | dB(A) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz
Daytime freefield Noise, L1in /dB(A) | 58.3087 | 42.8 | 47.4 | 51.5 | 54.6 | 52.4 | adjust 1 dB to get same value as sum of 6 octave
4/12/4/12/4 |  | 20 | 18 | 27 | 43 | 49
Equation 1, L2 /dB(A) | 29.3131 | 20.7778 | 27.3778 | 22.4778 | 9.5778 | 1.3778
SRI Wall Type A - insul |  | 48 | 51 | 58 | 65 | 70
Equation 2, L2 /dB(A) | 5.3539 | -0.14382 | 1.4562 | -1.4438 | -5.3438 | -12.5438
Combined noise through window and vent/ dB(A) | 29.3306
Octave centre frequency | dB(A) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz
Night time freefield noise, L1in /dB(A) | 50.6708 | 35.9 | 41.7 | 45.1 | 46.6 | 43
4/12/4/12/4 |  | 20 | 18 | 27 | 43 | 49
Equation 1, L2 /dB(A) | 23.2981 | 13.8778 | 21.6778 | 16.0778 | 1.5778 | -8.0222
SRI Wall Type A - insul |  | 48 | 51 | 58 | 65 | 70
Equation 2, L2 /dB(A) | -1.0189 | -7.0438 | -4.2438 | -7.8438 | -13.3438 | -21.9438
Combined noise through window and vent/ dB(A) | 23.3142

## NR 7-9-2015
Calculation of noise ratings from octave band data as described in BS 8233 Annex B
Copy NorXfer data into "Data"
Reference A-weighted and octave band data in cells D14:M14 and then copy row 14 down
|  | A-weighting (dB) | -39.4 | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | -6.6
Ocatve band centre frequency (Hz) |  | A | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  |  | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
Noise rating = (Leq - a) / b
a | [13 empty] | 55.4 | 35.4 | 22 | 12 | 4.2 | 0 | -3.5 | -6.1 | -8
b | [13 empty] | 0.681 | 0.79 | 0.87 | 0.93 | 0.98 | 1 | 1.015 | 1.025 | 1.03
[5 empty] | 125 | 250 | 500 | 1000 | 2000 |  |  |  | NR | corresponding NR for each OBCF value
| A-weighted |  |  |  | 14.1482 | 8.9016 | -3.4315 | -6.3725 | -10.4844
| Linea |  |  |  | 30.2482 | 17.5016 | -0.23153 | -6.3725 | -11.6844 |  |  |  | 10 |  |  | 9.4807 | 5.9157 | -4.522 | -6.3725 | -8.0635

## Corner room mechanical serv
[14 empty] | 12500 | 16000 | 20000 | A
Scenario 2 | [8 empty] | A-weighted sound pressure level / dB
Guest room at the corner | [8 empty] | Octave bands / Hz
Volume, V /m3 | 40.536 | [6 empty] | 125 | 250 | 500 | 1000 | 2000
Window area, S /m2 | 4.0425 | [5 empty] | NR 20 | 22.9 | 22.4 | 20.8 | 20 | 18.2 | 28.1628
Wall area, S /m2 | 20.6295 | [5 empty] | NR 40 | 40.9 | 40.4 | 40.8 | 40 | 38.2
Reverberation Time, T /s | 0.5 | [5 empty] | NR 50 | 49.9 | 50.4 | 49.8 | 50 | 48.2
Number of vents required | [6 empty] | NR 45 | 44.9 | 45.4 | 44.8 | 45 | 43.2
Octave centre frequency | dB(A) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz
A-weighted sound level of NR40, L1in /dB(A) | 47.1514 | 40.9 | 40.4 | 40.8 | 40 | 38.2
4/12/4/12/4 |  | 20 | 18 | 27 | 43 | 49
Equation 1, L2 /dB(A) | 23.048 | 18.8778 | 20.3778 | 11.7778 | -5.0222 | -12.8222
SRI Wall Type A - insul |  | 48 | 51 | 58 | 65 | 70
Equation 2, L2 /dB(A) | -0.10142 | -2.0438 | -5.5438 | -12.1438 | -19.9438 | -26.7438
Combined noise through window and vent/ dB(A) | 23.069 | 18.9128 | 20.3889 | 11.7954 | -4.8846 | -12.6496 | * the coresponding NR is shown in sheet NR
NR | 19
Scenario 1
Guest room at the corner
Volume, V /m3 | 40.536
Window area, S /m2 | 4.0425
Wall area, S /m2 | 20.6295
Reverberation Time, T /s | 0.5
Number of vents required
Octave centre frequency | dB(A) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz
A-weighted sound level of NR45, L1in /dB(A) | 51.7112 | 44.9 | 45.4 | 44.8 | 45 | 43.2
8.4 (44.1)/12/6/12/10 |  | 29 | 35 | 48 | 50 | 52
Equation 1, L2 /dB(A) | 15.0361 | 13.8778 | 8.3778 | -5.2222 | -7.0222 | -10.8222
SRI Wall Type A - insul |  | 48 | 51 | 58 | 65 | 70
Equation 2, L2 /dB(A) | 4.2215 | 1.9562 | -0.54382 | -8.1438 | -14.9438 | -21.7438
Combined noise through window and vent/ dB(A) | 15.382 | 14.1482 | 8.9016 | -3.4315 | -6.3725 | -10.4844
NR | 10

## Wall board
Octave band | 125 | 250 | 5000 | 1000 | 2000
SRI Wall Type A - insul | 48 | 51 | 58 | 65 | 70

## Speech spec
Sound power level
Octave bands central frequency
SWL shouted | A-weighted | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| 91 | 52 | 63 | 73 | 84 | 89.3 | 82.4 | 74.9 | 64.1

## LAeq1700-1800
LAeq / dB
Octave bands central frequency / Hz
Frequency [Hz] | LAeq | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
LAeq [dB] | 56.6 | 27.3 | 36 | 40.8 | 45.4 | 49.5 | 52.6 | 50.4 | 44.6 | 32.3

## LAeq1hr-night
|  | 2300-2400 |  | 2400-0100 |  | 0100-0200 |  | 0200-0300 |  | 0300-0400 |  | 0400-0500 |  | 0500-0600 | 0600-0700
| Marker RTA |  | Marker RTA |  | Marker RTA |  | Marker RTA |  | Marker RTA |  | Marker RTA |  | Marker RTA |  | Marker RTA
| Frequency [Hz] | LAeq [dB] | Frequency [Hz] | LAeq [dB] | Frequency [Hz] | LAeq [dB] | Frequency [Hz] | LAeq [dB] | Frequency [Hz] | LAeq [dB] | Frequency [Hz] | LAeq [dB] | Frequency [Hz] | LAeq [dB] | Frequency [Hz] | LAeq [dB]
| 31.5 | 15.9 | 31.5 | 12.9 | 31.5 | 13.2 | 31.5 | 15.8 | 31.5 | 14.9 | 31.5 | 15.8 | 31.5 | 15.1 | 31.5 | 18.8
| 63 | 27.6 | 63 | 25.5 | 63 | 26 | 63 | 26.6 | 63 | 27.8 | 63 | 28.3 | 63 | 29.1 | 63 | 30.4
| 125 | 31 | 125 | 31.6 | 125 | 32.2 | 125 | 34.3 | 125 | 33.6 | 125 | 33.7 | 125 | 34 | 125 | 34.9
| 250 | 38.2 | 250 | 38.8 | 250 | 39.4 | 250 | 39.7 | 250 | 38.3 | 250 | 38.1 | 250 | 40.3 | 250 | 40.7
| 500 | 44 | 500 | 42.7 | 500 | 43.2 | 500 | 44 | 500 | 42.3 | 500 | 41.4 | 500 | 44.2 | 500 | 44.1
| 1000 | 46.5 | 1000 | 44 | 1000 | 44.4 | 1000 | 45.3 | 1000 | 43.7 | 1000 | 45.7 | 1000 | 46.8 | 1000 | 45.6
| 2000 | 43.2 | 2000 | 39.2 | 2000 | 40.4 | 2000 | 41.9 | 2000 | 40.5 | 2000 | 42 | 2000 | 44.2 | 2000 | 42
| 4000 | 35.7 | 4000 | 31.1 | 4000 | 32.3 | 4000 | 34.1 | 4000 | 37 | 4000 | 37.7 | 4000 | 38.7 | 4000 | 37
| 8000 | 20.6 | 8000 | 16.5 | 8000 | 17.2 | 8000 | 18.9 | 8000 | 21.5 | 8000 | 22.8 | 8000 | 22.9 | 8000 | 25.9
LAeq |  | 50.1 |  | 48 |  | 48.6 |  | 49.5 |  | 48.2 |  | 49.2 |  | 50.8 |  | 50

## SWL-seagulls
LAFmax of seagull at 15 m
[8 empty] | LAeq_dt / dB | [10 empty] | LAFmax_dt / dB
[8 empty] | Octave bands central frequency / Hz | [10 empty] | Octave bands central frequency / Hz
|  | LAFmax_dt | LAeq_dt | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | LAFmax_dt | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
|  | 71.8 | 68.6 | 23.4 | 31.3 | 39.3 | 42.5 | 45.5 | 66.7 | 62.4 | 53.3 | 39.7 |  | 71.8 | 26.6 | 34.5 | 42.5 | 45.7 | 48.7 | 69.9 | 65.6 | 56.5 | 42.9
|  | 73.2 | 69.2 | 24 | 32.4 | 39 | 39.8 | 46.4 | 68.6 | 58.1 | 52.9 | 42.8 |  | 73.2 | 28 | 36.4 | 43 | 43.8 | 50.4 | 72.6 | 62.1 | 56.9 | 46.8
|  | 72.8 | 68.3 | 20.8 | 32.6 | 40 | 40.9 | 45.2 | 66.8 | 62 | 55 | 40.5 |  | 72.8 | 25.3 | 37.1 | 44.5 | 45.4 | 49.7 | 71.3 | 66.5 | 59.5 | 45
|  | 73 | 66.9 | 20.4 | 34.8 | 38.6 | 38.5 | 44.6 | 64.7 | 61.3 | 57.5 | 42.9 |  | 73 | 26.5 | 40.9 | 44.7 | 44.6 | 50.7 | 70.8 | 67.4 | 63.6 | 49
|  | 72.1 | 69 | 26.1 | 30 | 37.8 | 40.3 | 46.2 | 68.2 | 58.6 | 56.8 | 45.2 |  | 72.1 | 29.2 | 33.1 | 40.9 | 43.4 | 49.3 | 71.3 | 61.7 | 59.9 | 48.3
| Arithmatic mean |  | 68.4 | 22.94 | 32.22 | 38.94 | 40.4 | 45.58 | 67 | 60.48 | 55.1 | 42.22 | Arithmatic mean | 72.58 | 27.12 | 36.4 | 43.12 | 44.58 | 49.76 | 71.18 | 64.66 | 59.28 | 46.4
SWL | Lw = Lp + 20*log r + 11
LW / dB(A)
Octave bands central frequency / Hz
|  |  | LW | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
|  |  | 107.1018 | 61.6418 | 70.9218 | 77.6418 | 79.1018 | 84.2818 | 105.7018 | 99.1818 | 93.8018 | 80.9218

## Double
Pilkintons Glazing Data |  |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
Double Glazing | 4-16-4 |  | 20 | 24 | 20 | 25 | 35 | 38 | 35 | 40
| 6-16-6 |  | 18 | 20 | 19 | 29 | 38 | 36 | 45 | 45
| 6-16-6.4PVB |  | 19 | 21 | 20 | 31 | 39 | 37 | 47 | 47
| 10-16-4 |  | 21 | 25 | 22 | 33 | 40 | 43 | 44 | 44
| 10-16-6 |  | 22 | 26 | 27 | 34 | 40 | 38 | 46 | 46
| 10-16-6.4PVB |  | 23 | 27 | 29 | 36 | 41 | 42 | 52 | 52
Nordan Glazing Data |  |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| 4-16-6 |  | 19 | 19 | 22 | 24 | 34 | 41 | 40 | 40
BS 12758 | Rw | 125 | 250 | 500 | 1000 | 2000 | 4000 |  | C | Ctr
Glazing: 4/(6-16)/4 | 29 | 21 | 17 | 25 | 35 | 37 | 31 |  | -1 | -4
Glazing: 6/(6-16)/4 | 32 | 21 | 20 | 26 | 38 | 37 | 39 |  | -2 | -4
Glazing: 6/(6-16)/6 | 31 | 20 | 18 | 28 | 38 | 34 | 38 |  | -1 | -4
Glazing: 8/(6-16)/4 | 33 | 22 | 21 | 28 | 38 | 40 | 47 |  | -1 | -4
Glazing: 8/(6-16)/6 | 35 | 20 | 21 | 33 | 40 | 36 | 48 |  | -2 | -6
Glazing: 10/(6-16)/4 | 35 | 24 | 21 | 32 | 37 | 42 | 43 |  | -2 | -5
Glazing: 10/(6-16)/6 | 35 | 24 | 24 | 32 | 37 | 37 | 44 |  | -1 | -3
Glazing: 6/(6-16)/6 Laminated | 33 | 20 | 19 | 30 | 39 | 37 | 46 |  | -2 | -5
Glazing: 6/(6-16)/10 Laminated | 37 | 24 | 25 | 33 | 39 | 40 | 49 |  | -1 | -5
Product Description: | Polycarbonate |  |  |  | SGG Data from acoustic presentation
Third Octave Data: |  | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000
[5 empty] | 10 | 9 | 11 | 14 | 16 | 18 | 18 | 18 | 20 | 21 | 23 | 24 | 24 | 24 | 23 | 16 | 20 | 31
Calculated Octave Data |  |  |  |  | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
16 mm Polycarbonate |  |  |  |  | 9.9236 | 15.6983 | 18.5701 | 22.483 | 23.6405 | 19.2187
Reported Overall figures:
Rw | 21

## Acoustic
Pilkintons Glazing Data |  | 125 | 250 | 500 | 1000 | 2000 | 4000
Acoustic Glazing | 6.8 | 26 | 27 | 31 | 36 | 40 | 39
| 8.8 | 24 | 28 | 34 | 38 | 37 | 43
| 9.1 | 26 | 29 | 34 | 38 | 38 | 43
| 12.8 | 30 | 32 | 37 | 39 | 41 | 51
| 13.1 | 30 | 33 | 37 | 40 | 41 | 50
| 6/16/6.8 | 22 | 27 | 35 | 42 | 41 | 48
| 6/16/8.8 | 24 | 26 | 40 | 48 | 46 | 54
| 8/16/9.1 | 24 | 29 | 41 | 47 | 47 | 55
| 10/16/9.1 | 29 | 33 | 44 | 46 | 49 | 57
| 8.8/16/12.8 | 26 | 36 | 46 | 50 | 52 | 63
| 9.1/20/13.1 | 29 | 39 | 49 | 52 | 55 | 63

## Guardian Triple
Type | Glazing Construction | Interlayer | Overall | Glazing | Glass/Unit Performance |  |  | Octave Centre Frequency Performance | [5 empty] | Certificate Type
|  |  | Thickness (mm) | Type | Rw [dB] | Rw + C | Rw + Ctr [dB] | 125 | 250 | 500 | 1000 | 2000 | 4000
34-34 K | 4/10/4/10/6 | x | 34 | Triple | 34 | 33 | 29 | 22 | 21 | 33 | 49 | 46 | 49 | Certified
36-31 A | 4/12/4/12/4 | x | 36 | Triple | 31 | 30 | 26 | 20 | 18 | 27 | 43 | 49 | 43 | Certified
36-33 K | 4/12/4/12/4 | x | 36 | Triple | 33 | 32 | 28 | 22 | 20 | 33 | 47 | 47 | 42 | Certified
38-35 A | 4/12/4/12/6 | x | 38 | Triple | 35 | 34 | 30 | 22 | 24 | 32 | 46 | 47 | 47 | Certified
38-36 K | 4/12/4/12/6 | x | 38 | Triple | 36 | 34 | 30 | 20 | 24 | 35 | 48 | 44 | 50 | Certified
40-36 A | 4/12/4/12/8 | x | 40 | Triple | 36 | 34 | 30 | 21 | 24 | 33 | 44 | 48 | 51 | Certified
40-31 A | 4/14/4/14/4 | x | 40 | Triple | 31 | 30 | 26 | 20 | 19 | 28 | 42 | 48 | 42 | Certified
44-32 A | 4/16/4/16/4 | x | 44 | Triple | 32 | 31 | 27 | 18 | 20 | 29 | 44 | 50 | 43 | Certified
42-38 A | 6/12/4/12/8 | x | 42 | Triple | 38 | 37 | 33 | 21 | 28 | 37 | 43 | 41 | 55 | Certified
42-38 K | 6/12/4/12/8 | x | 42 | Triple | 38 | 36 | 33 | 21 | 28 | 39 | 45 | 39 | 54 | Certified
43-41 A | 6/12/4/12/8.8 (44.2) | SC | 43 | Triple | 41 | 39 | 35 | 23 | 31 | 39 | 49 | 48 | 59 | Certified
43-41 K | 6/12/4/12/8.8 (44.2) | SC | 43 | Triple | 41 | 39 | 35 | 23 | 30 | 42 | 51 | 46 | 60 | Certified
47-43 A | 6/14/4/14/8.4 (44.1) | SC | 47 | Triple | 43 | 42 | 36 | 24 | 33 | 41 | 52 | 52 | 61 | Certified
48-37 A | 6/14/8.4 (44.1)/14/6 | SC | 48 | Triple | 37 | 35 | 32 | 21 | 26 | 37 | 44 | 37 | 49 | Certified
45-42 A | 8/12/4/12/8.8 (44.2) | SC | 45 | Triple | 42 | 40 | 36 | 19 | 29 | 41 | 46 | 43 | 59 | Certified
45-42 A | 8/12/4/12/8.8 (44.2) | SC | 45 | Triple | 42 | 40 | 36 | 24 | 31 | 40 | 48 | 47 | 60 | Certified
45-41 K | 8/12/4/12/8.8 (44.2) | SC | 45 | Triple | 41 | 39 | 35 | 24 | 30 | 42 | 49 | 46 | 62 | Certified
46-43 A | 8/12/5/12/8.8 (44.2) | SC | 46 | Triple | 43 | 40 | 36 | 24 | 32 | 41 | 49 | 47 | 58 | Certified
47-44 A | 8/12/6/12/8.4 (44.1) | SC | 47 | Triple | 44 | 42 | 37 | 25 | 32 | 42 | 50 | 52 | 61 | Certified
48-47 K | 8.4 (44.1)/12/6/12/10 | SC | 48 | Triple | 47 | 45 | 40 | 29 | 35 | 48 | 50 | 52 | 59 | Certified
48-46 A | 8.4 (44.1)/12/6/12/10 | SC | 48 | Triple | 46 | 44 | 39 | 28 | 35 | 43 | 51 | 52 | 60 | Certified
50-47 A | 8.8 (44.2)/12/6/12/10.8 (55.2) | SC/SC | 50 | Triple | 47 | 45 | 40 | 29 | 34 | 45 | 53 | 54 | 66 | Certified
50-47 K | 8.8 (44.2)/12/6/12/10.8 (55.2) | SC/SC | 50 | Triple | 47 | 44 | 40 | 28 | 34 | 48 | 55 | 53 | 69 | Certified
66-53 | 10.8 (55.2)/16/6/16/16.8 (88.2) | SC/SC | 66 | Triple | 53 | 51 | 47 | 36 | 40 | 50 | 55 | 61 | 65 | Certified
guardianglass.co.uk 14/04/2015

## NR
Calculation of noise ratings from octave band data as described in BS 8233 Annex B
Copy NorXfer data into "Data"
Reference A-weighted and octave band data in cells D14:M14 and then copy row 14 down
|  | A-weighting (dB) | -39.4 | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | -6.6
Ocatve band centre frequency (Hz) |  | A | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  |  | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
Noise rating = (Leq - a) / b
a | [13 empty] | 55.4 | 35.4 | 22 | 12 | 4.2 | 0 | -3.5 | -6.1 | -8
b | [13 empty] | 0.681 | 0.79 | 0.87 | 0.93 | 0.98 | 1 | 1.015 | 1.025 | 1.03
|  | LAeq | Leq at OBCF | [9 empty] | NR | corresponding NR for each OBCF value
|  |  |  | 46.5 | 40.4 | 32.6 | 27.8 | 22.6 | 17 | 12.4 | 13.2 |  | 24.0816 | -81.351 | 14.0506 | 21.1494 | 22.1505 | 24.0816 | 22.6 | 20.197 | 18.0488 | 20.5825
| A-weighted | Scenario 2 |  |  | 18.9128 | 20.3889 | 11.7954 | -4.8846 | -12.6496
|  | Scenario 1 |  |  | 19.1482 | 13.9016 | 1.5685 | -1.3725 | -5.4844
| Linea | Scenario 2 |  |  | 35.0128 | 28.9889 | 14.9954 | -4.8846 | -13.8496 |  |  |  | 19 |  |  | 14.9572 | 18.2676 | 11.0157 | -4.8846 | -10.1967
|  | Scenario 1 |  |  | 35.2482 | 22.5016 | 4.7685 | -1.3725 | -6.6844 |  |  |  | 16 |  |  | 15.2278 | 11.292 | 0.58007 | -1.3725 | -3.1374

## NR - dB(A)
A-weightings |  | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
Hz | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | Hz | NR75 | NR70 | NR65 | NR60 | NR55 | NR50 | NR45 | NR40 | NR35 | NR30 | NR25 | NR20 | NR15 | NR10 | NR5 | NR0
NR75 | 106 | 95 | 87 | 82 | 78 | 75 | 73 | 71 | 69 |  | 31.5 | 106 | 103 | 100 | 96 | 93 | 89 | 86 | 83 | 79 | 76 | 72 | 69 | 66 | 62 | 59 | 55
NR70 | 103 | 91 | 83 | 77 | 73 | 70 | 68 | 66 | 64 |  | 63 | 95 | 91 | 87 | 83 | 79 | 75 | 71 | 67 | 63 | 59 | 55 | 51 | 47 | 43 | 39 | 35
NR65 | 100 | 87 | 79 | 72 | 68 | 65 | 62 | 61 | 59 |  | 125 | 87 | 83 | 79 | 74 | 70 | 66 | 61 | 57 | 52 | 48 | 44 | 39 | 35 | 31 | 26 | 22
NR60 | 96 | 83 | 74 | 68 | 63 | 60 | 57 | 55 | 54 |  | 250 | 82 | 77 | 72 | 68 | 63 | 59 | 54 | 49 | 45 | 40 | 35 | 31 | 26 | 21 | 17 | 12
NR55 | 93 | 79 | 70 | 63 | 58 | 55 | 52 | 50 | 49 |  | 500 | 78 | 73 | 68 | 63 | 58 | 53 | 48 | 44 | 39 | 34 | 29 | 24 | 19 | 15 | 10 | 5
NR50 | 89 | 75 | 66 | 59 | 53 | 50 | 47 | 45 | 43 |  | 1000 | 75 | 70 | 65 | 60 | 55 | 50 | 45 | 40 | 35 | 30 | 25 | 20 | 15 | 10 | 5 | 0
NR45 | 86 | 71 | 61 | 54 | 48 | 45 | 42 | 40 | 38 |  | 2000 | 73 | 68 | 62 | 57 | 52 | 47 | 42 | 37 | 32 | 27 | 22 | 17 | 12 | 7 | 2 | 24
NR40 | 83 | 67 | 57 | 49 | 44 | 40 | 37 | 35 | 33 |  | 4000 | 71 | 66 | 61 | 55 | 50 | 45 | 40 | 35 | 30 | 25 | 20 | 14 | 9 | 4 | 21 | 26
NR35 | 79 | 63 | 52 | 45 | 39 | 35 | 32 | 30 | 28 |  | 8000 | 69 | 64 | 59 | 54 | 49 | 43 | 38 | 33 | 28 | 23 | 18 | 13 | 7 | 2 | 23 | 28
NR30 | 76 | 59 | 48 | 40 | 34 | 30 | 27 | 25 | 23
NR25 | 72 | 55 | 44 | 35 | 29 | 25 | 22 | 20 | 18
NR20 | 69 | 51 | 39 | 31 | 24 | 20 | 17 | 14 | 13
NR15 | 66 | 47 | 35 | 26 | 19 | 15 | 12 | 9 | 7
NR10 | 62 | 43 | 31 | 21 | 15 | 10 | 7 | 4 | 2
NR5 | 59 | 39 | 26 | 17 | 10 | 5 | 2 | 21 | 23
NR0 | 55 | 35 | 22 | 12 | 5 | 0 | 24 | 26 | 28
NR | 55.4 | 35.4 | 22 | 12 | 4.2 | 0 | -3.5 | -6.1 | -8 | a
30 | 0.681 | 0.79 | 0.87 | 0.93 | 0.98 | 1 | 1.015 | 1.025 | 1.03 | b
| 75.83 | 59.1 | 48.1 | 39.9 | 33.6 | 30 | 26.95 | 24.65 | 22.9
NR 20 |  | 24.8 | 22.9 | 22.4 | 20.8 | 20 | 18.2 | 15
NR 30
NR 40 |  | 40.8 | 40.9 | 40.4 | 40.8 | 40 | 38.2 | 36
NR 50 |  |  | 49.9 | 50.4 | 49.8 | 50 | 48.2
NR 45 |  |  | 44.9 | 45.4 | 44.8 | 45 | 43.2 | * update on 7/9/2015